## Slide 1
MACRO-Korea: open technical questions
Provincial power-sector model · 17 provinces · 8,760 chronological hours · 2021–2050 myopic

## Slide 2
Agenda
2021 Calibration issue - after changed the transmission
Capacity expansion and generation by tech (Ref vs NDC) – diagnosis
Renewable energy expansion rate - Can we limit a national build rate?
Unit commitment parameter - How should nuclear and MinFlow be configured?
Carbon price (related to nuclear) - Is the carbon price real?
Notes: Five things. We'll start with where the base year stands, because there's a known gap and I want to flag it before you see any numbers.
Then capacity and generation for both scenarios so you have the picture.
Then three questions: the renewable build rate, the unit commitment parameters, and the carbon price.

## Slide 3
STATUS
Where the model is
Structure
Complete. 7 periods, 8,760 h, linear-relaxed UC, myopic, Gurobi barrier.
Solve
Ref 2.5 h · NDC 4.6 h on 24 cores / 192 GB. ~13.6M rows.
Transmission
99.1 GW network from NREL ITLs, calibrated to the KPX metro limit. Expands.
Base year
NOT calibrated. Coal 300 TWh vs 198 observed; gas 58 vs 167.
Staged fixes
Coal availability 0.65 · nuclear 0.85→0.78 · 2021 gas retirement blocked.
Notes: Structurally we're complete. Seven periods, 8,760 chronological hours, linearly relaxed unit commitment, myopic, Gurobi barrier. About 13.6 million rows. Ref solves in two and a half hours, NDC in four and a half, on 24 cores.
Transmission is in good shape. We built a 99 gigawatt inter-province network from NREL interface transfer limits, calibrated to the KPX metro import limit, and it now expands — which it never did before.
The base year is not calibrated. We can check about this next slide.

## Slide 4
CONTEXT
The results you are about to see predate the base-year fix
Flagged so the known gap is not re-diagnosed. Fixes are staged, not yet run.
Notes: Here's that gap. Coal and gas are inverted.
The cause is simple: coal and gas carried no availability field at all, so both defaulted to 1.0 — available every hour of the year, no maintenance, no outages, no seasonal curtailment. Coal is half the variable cost of gas, so nothing stopped it running at a 95% capacity factor and taking gas's work.
Three fixes are staged. Coal availability at 0.65, nuclear from 0.85 down to 0.78, and blocking a gas retirement the model was making in the calibration year itself. I'm flagging this so we don't spend the meeting re-diagnosing it.

## Slide 5
CONTEXT

## Slide 6
QUESTION 1 · HIGHEST PRIORITY
MaxNewCapacityConstraint is per-asset, so we cannot cap a national build rate
We need ≤ 5 GW/yr nationally. The only lever is 6,000 MW per province per period. Is a grouped MaxNewCapacityConstraint available upstream?
Notes: We capped each province at 6 GW per five-year period. The national total came out at 6 GW per year. Same number, but one is a per-province input and the other is a national result.

## Slide 7
QUESTION 2
MinFlowConstraint on all five thermal technologies ran us out of memory
Rows, MinFlow on coal + gas CCGT only
13.60 M
Rows, MinFlow on all five
14.05 M
Added by three technologies
≈ 450,000 rows
Outcome at 128 GB
killed — two jobs
Current state
off for nuclear, coal CCS, gas CCS; mem raised to 192 GB
min_flow_fraction values are still in the CSVs for those three technologies but the constraint is not declared.
Is that row growth expected? Is there a cheaper MinFlow formulation under relaxed UC — and are the undeclared min_flow_fraction values truly inert?

## Slide 8
QUESTION 2
Nuclear

## Slide 9
QUESTION 3
Nuclear is completely rigid, and the carbon price absorbs the consequence
What is the idiomatic way to represent near-baseload nuclear in MACRO? Drop MustRun for a low min_flow_fraction instead?
Notes: Nuclear is held at a fixed 85% in every hour of every year — MustRun makes it an equality, not a floor. It can't move when solar floods the grid, so the model curtails 51 terawatt-hours and the carbon price goes to several thousand dollars. Korea actually curtails nuclear today and KHNP is targeting a 50% minimum by the 2030s, so we're modelling it as less flexible than it already is. We'll replace MustRun with a declining minimum-output floor.

## Slide 10
SUMMARY
What we are asking for
1
Grouped MaxNewCapacityConstraint
unblocks every build-rate limit we need
2
A cheaper MinFlow formulation
or confirmation that 450k rows is simply the cost